| Project No.: | 01-26-020 (26766) | RFI No.: | RFI-126020-012 |
| --- | --- | --- | --- |
| Date: | August 25, 2026 | Discipline: | Piping |
| Project Name: | 26766 – BA2107 TLE End-of-Life Replacement |  |  |

| Subject: | ASC Fig. 40 Riser Clamps – Level Bridle Piping |
| --- | --- |
| Specifications/Documents/Drawings Referenced or Impacted: |  |
| Isometric FA2107-TRIM Rev. 1.1, Sheets 1 and 2, Note 9 ASC Fig. 40 Riser Clamp – Standard, data sheet ASC Fig. 261 Extension Pipe or Riser Clamp, data sheet |  |

| Question or Description of Issue: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Note 9 of isometric FA2107-TRIM Rev. 1.1, Sheets 1 and 2, specifies ASC Fig. 40 riser clamps on the FA-2107 level bridle piping. Note 9 states: “REMOVE INSULATION AND INSTALL CS ASC RISER CLAMP FIG.40. RISER SHOULD REST ON STEEL. RE-INSULATE PIPING TO MATCH EXISTING.” The 4" Fig. 40 clamps are quoted at $822.39 each and are not available until early November. ASC originally quoted Fig. 261 clamps, which are available from stock but carry a lower rating: at 4" NPS the Fig. 40 is rated 2,200 lb in a rigid assembly against 750 lb for the Fig. 261. The ASC data sheet for the Fig. 40 also states that load is carried by shear lugs welded to the pipe. Shear lugs are not identified or detailed on the scope drawings, and Note 9 instead indicates that the riser is to rest on steel. Welding shear lugs to the FA-2107 trim piping (4"/2", pipe class 15CS03C, 1950 psig at 650°F, ASME B31.3 normal fluid service) would introduce additional welding, examination and hydrotest requirements beyond those currently shown. |  |  |  |  |  |  |  |  |
| Originator’s Recommended Solution: |  |  |  |  |  |  |  |  |
| Please review the required support and restraint loads for the level bridle piping and advise whether ASC Fig. 261 clamps are acceptable in lieu of the specified Fig. 40. If the Fig. 261 is not acceptable, please advise whether a field-fabricated support such as angle iron with a tight U-bolt or similar arrangement may be used in order to avoid welding to the existing piping. Please also confirm whether shear lugs are required and, if so, issue the applicable detail together with the associated examination and test requirements. |  |  |  |  |  |  |  |  |
| Urgency: | Medium (3 days) |  |  |  |  |  |  |  |
| Originator: |  |  |  |  |  |  |  |  |
|  | Nitin Joshi |  |  |  | PC |  | August 25, 2026 |  |
|  | Name |  | Signature |  | Title |  | Date |  |

| Response: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Respondent: |  |  |  |  |  |  |  |  |
|  | Name |  | Signature |  | Title |  | Date |  |