| Project No.: | 01-26-020 (26766) | RFI No.: | RFI-126020-010 |
| --- | --- | --- | --- |
| Date: | August 25, 2026 | Discipline: | Structural |
| Project Name: | 26766 – BA2107 TLE End-of-Life Replacement |  |  |

| Subject: | TLE Channel Cover Lifting Lugs |
| --- | --- |
| Specifications/Documents/Drawings Referenced or Impacted: |  |
| 26766 - CWP-G02 Rev 0.1 - 2021489 – IFC, Section 6.1.9 EA2102D-049 Rev 0.2, “EA-2102D New Lifting Lug Installation” (Work Package, page 92) |  |

| Question or Description of Issue: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Section 6.1.9 of the Construction Work Package requires the existing channel cover lifting lugs to be used to lift TLEs EA-2107A, B and C. Section 6.1.9 states: “Use the existing lifting lug on the top of each TLE’s channel cover to lift existing TLEs tag # EA-2107A, B & C from heater BA-2107. Refer to drawing number EA2102D-049. The cover lifting lugs have a combined vertical lifting capacity of 43,042 lbs. These cover lifting lugs were installed on EA-2107A & B in 2022. One of these covers can be used to replace the cover on EA-2107C after EA-2107A&B have been removed.” Field review of the existing TLEs found no channel covers with lifting lugs installed in the configuration specified by Section 6.1.9. Drawing EA2102D-049 Rev 0.2 records a single installation. Note 10 states: “This change is implemented in April 2022, when EA-2102D channel is installed on EA-2107B TLE tube section. These lifting lugs have been designed for this configuration only. Any future change must be re-evaluated by engineering.” The drawing therefore accounts for lugs on EA-2107B only, not on EA-2107A as stated in Section 6.1.9, and Note 10 appears to require engineering re-evaluation before a lugged cover is transferred to EA-2107C. Note 7 of the same drawing rates each lug at 21,521 lb in-plane only. The 43,042 lb figure in Section 6.1.9 is the sum of the two in-plane ratings and is stated as a vertical lifting capacity. |  |  |  |  |  |  |  |  |
| Originator’s Recommended Solution: |  |  |  |  |  |  |  |  |
| Please confirm the location and installation records of the existing cover lifting lugs and issue the applicable drawings. If lugs to EA2102D-049 are not installed on EA-2107A, B and C, please advise the lifting method to be used and whether design and installation of new lugs is a change to scope. Please also confirm the sling arrangement required to keep each lug loaded in-plane, and that engineering re-evaluation under Note 10 will be provided for reuse of a cover on EA-2107C. |  |  |  |  |  |  |  |  |
| Urgency: | Medium (3 days) |  |  |  |  |  |  |  |
| Originator: |  |  |  |  |  |  |  |  |
|  | Nitin Joshi |  |  |  | PC |  | August 25, 2026 |  |
|  | Name |  | Signature |  | Title |  | Date |  |

| Response: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Respondent: |  |  |  |  |  |  |  |  |
|  | Name |  | Signature |  | Title |  | Date |  |